## Fleet Expiration Tracker
CellFit UPS: Fleet Battery Expiration Tracker
Fill in the yellow columns: pick your UPS from the dropdown and enter its install date. The rest fills itself in.
36 months is a planning interval, not an OEM figure. Heat and frequent outages shorten it. LiFePO4 ceilings assume a 12 A BMS and 82% inverter efficiency. Specs verified 2026-11-02; see https://cellfitups.com/data/.
Asset / Location | UPS Model | Serial Number | Install Date | OEM Cartridge SKU | Bare Cell Count & Spec | Max DC Amps | LiFePO4 Ceiling at 12 A BMS (W) | 36-Month Replacement Due | Status | Order | Model Page | Serial Split

## Verified Model & Cartridge Ref
UPS Model | Brand | OEM Cartridge SKU | Bare Cell Count & Spec | Max DC Amps | LiFePO4 Ceiling at 12 A BMS (W) | Terminal | Cell Count Evidence | Serial Split | CellFit Page | Order Link Label
BR1500MS2 | APC | APCRBC163 | 2 x 12V 9.4Ah F2 | 45.7 | 236 | F2 | inferred | No serial split found | https://cellfitups.com/ups/br1500ms2/ | Order Bare Cells
BX1500M | APC | APCRBC124 | 2 x 12V 9Ah F2 | 45.7 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/bx1500m/ | Order Bare Cells
BR1500G | APC | APCRBC124 | 2 x 12V 9Ah F2 | 44 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/br1500g/ | Order Bare Cells
BN1500M2 | APC | APCRBC161 | 2 x 12V 9Ah F2 | 45.7 | 236 | F2 | inferred | No serial split found | https://cellfitups.com/ups/bn1500m2/ | Order Bare Cells
BE600M1 | APC | APCRBC154 | 1 x 12V 6.5Ah +F2/-F1 | 33.5 | No verified LiFePO4 fit | +F2/-F1 | verified | No serial split found | https://cellfitups.com/ups/be600m1/ | Order Bare Cells
BE850G2 | APC | RBC17 | 1 x 12V 9Ah F2 | 45.7 | 118 | F2 | verified | No serial split found | https://cellfitups.com/ups/be850g2/ | Order Bare Cells
SMT1500C | APC | RBC7 | 2 x 12V 17Ah NB | 50.8 | No verified LiFePO4 fit | NB | inferred | No serial split found | https://cellfitups.com/ups/smt1500c/ | Order Bare Cells
CP1500PFCLCD | CyberPower | RB1290X2 | 2 x 12V 9Ah F2 | 50.8 | 236 | F2 | verified | Check your serial first. Serial starts CXX: RB1290X2, 2 x 12V 9 Ah, 150 x 66 x 99 mm. Serial starts CR9, CXF or CQC: RB1280X2B, a 202 x 64 x 151 mm pack. It looks like the same 151 x 65 mm cells laid on their sides, but measure yours first. | https://cellfitups.com/ups/cp1500pfclcd/ | Order Bare Cells
CP1500AVRLCD3 | CyberPower | RB1290X2E | 2 x 12V 9Ah F2 | 45.7 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/cp1500avrlcd3/ | Order Bare Cells
CP1350PFCLCD | CyberPower | RB1270X2C | 2 x 12V 7Ah F2 | 44.7 | 236 | F2 | verified | Check your serial first. Serial starts CXY or CX5: RB1270X2C, 2 x 12V 7 Ah, 99 x 66 x 150 mm. Takes 9 Ah cells in the same case for +28.6% capacity. Serial starts CQB or CR8: RB1270X2A, two 90 mm cube cells in a 180 x 70 x 106 mm pack. Standard 151 mm 7 Ah or 9 Ah batteries will not fit this tray. | https://cellfitups.com/ups/cp1350pfclcd/ | Order Bare Cells
CP1000PFCLCD | CyberPower | RB1290 | 1 x 12V 9Ah F2 | 61 | 118 | F2 | verified | No serial split found | https://cellfitups.com/ups/cp1000pfclcd/ | Order Bare Cells
EC850LCD | CyberPower | RB1270B | 1 x 12V 7.2Ah F2 | 51.8 | 118 | F2 | verified | No serial split found | https://cellfitups.com/ups/ec850lcd/ | Order Bare Cells
BR1000MS | APC | APCRBC160 | 2 x 12V 7Ah F2 | 30.5 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/br1000ms/ | Order Bare Cells
BX1000M | APC | APCRBC158 | 1 x 12V 9Ah F2 | 61 | 118 | F2 | verified | No serial split found | https://cellfitups.com/ups/bx1000m/ | Order Bare Cells
BE425M | APC | None sold | Not user replaceable | 25.9 | No verified LiFePO4 fit | Unverified | inferred | No serial split found | https://cellfitups.com/ups/be425m/ | See Model Page
SMT1500RM2UC | APC | APCRBC159 | 4 x 12V 9Ah F2 | 50.8 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/smt1500rm2uc/ | Order Bare Cells
SMT2200C | APC | RBC55 | 4 x 12V 17Ah NB | 50.3 | No verified LiFePO4 fit | NB | inferred | No serial split found | https://cellfitups.com/ups/smt2200c/ | Order Bare Cells
OR1500LCDRM2U | CyberPower | RB1270X4 | 4 x 12V 7Ah F2 | 45.7 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/or1500lcdrm2u/ | Order Bare Cells
SMART1500LCD | Tripp Lite | RBC1500 | 2 x 12V 7Ah F2 | 45.7 | 236 | F2 | inferred | No serial split found | https://cellfitups.com/ups/smart1500lcd/ | Order Bare Cells
5S1500LCD | Eaton | Eaton 5S cell pair | 2 x 12V 9Ah F2 | 45.7 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/5s1500lcd/ | Order Bare Cells
BR1350MS | APC | APCRBC161 | 2 x 12V 9Ah F2 | 41.2 | 236 | F2 | inferred | No serial split found | https://cellfitups.com/ups/br1350ms/ | Order Bare Cells
BR1000G | APC | APCRBC123 | 2 x 12V 7Ah F2 | 30.5 | 236 | F2 | inferred | No serial split found | https://cellfitups.com/ups/br1000g/ | Order Bare Cells
BX1350M | APC | APCRBC123 | 2 x 12V 7Ah F2 | 41.2 | 236 | F2 | inferred | No serial split found | https://cellfitups.com/ups/bx1350m/ | Order Bare Cells
BX850M | APC | RBC17 | 1 x 12V 9Ah F2 | 51.8 | 118 | F2 | verified | No serial split found | https://cellfitups.com/ups/bx850m/ | Order Bare Cells
BN1100M2 | APC | APCRBC160 | 2 x 12V 7Ah F2 | 30.5 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/bn1100m2/ | Order Bare Cells
BE650G1 | APC | RBC17 | 1 x 12V 9Ah F2 | 39.6 | 118 | F2 | verified | No serial split found | https://cellfitups.com/ups/be650g1/ | Order Bare Cells
CP1000AVRLCD | CyberPower | RB1290 | 1 x 12V 9Ah F2 | 61 | 118 | F2 | verified | No serial split found | https://cellfitups.com/ups/cp1000avrlcd/ | Order Bare Cells
CP850PFCLCD | CyberPower | RB1290 | 1 x 12V 9Ah F2 | 51.8 | 118 | F2 | verified | Check your serial first. Serial starts CX2: RB1290, 1 x 12V 9 Ah. Serial starts CQD: RB1280A, 1 x 12V 9 Ah. Same cell format, different SKU. | https://cellfitups.com/ups/cp850pfclcd/ | Order Bare Cells
LX1500GU | CyberPower | RB1290X2 | 2 x 12V 9Ah F2 | 45.7 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/lx1500gu/ | Order Bare Cells
CST1500SUC | CyberPower | RB1290X2 | 2 x 12V 9Ah F2 | 45.7 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/cst1500suc/ | Order Bare Cells
SMC1500-2UC | APC | APCRBC157 | 4 x 12V 7.2Ah F2 | 45.7 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/smc1500-2uc/ | Order Bare Cells
SMT750RM2UC | APC | APCRBC123 | 2 x 12V 7Ah F2 | 25.4 | 236 | F2 | inferred | No serial split found | https://cellfitups.com/ups/smt750rm2uc/ | Order Bare Cells
OR700LCDRM1U | CyberPower | RB0690X2 | 2 x 6V 8Ah F2 | 40.7 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/or700lcdrm1u/ | Order Bare Cells
CP1500PFCRM2U | CyberPower | RB1290X2D | 2 x 12V 9Ah F2 | 50.8 | 236 | F2 | verified | No serial split found | https://cellfitups.com/ups/cp1500pfcrm2u/ | Order Bare Cells
5P1500R | Eaton | EBP-0807 | 6 x 6V 9Ah F2 | 37.3 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/5p1500r/ | Order Bare Cells
PR1500LCDRTXL2U | CyberPower | RB1290X4F | 4 x 12V 9Ah F2 | 38.1 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/pr1500lcdrtxl2u/ | Order Bare Cells
PR2200LCDRT2U | CyberPower | RB1290X4F | 4 x 12V 9Ah F2 | 50.3 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/pr2200lcdrt2u/ | Order Bare Cells
PR1000LCDRT2U | CyberPower | RB1270X4F | 4 x 12V 7Ah F2 | 22.9 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/pr1000lcdrt2u/ | Order Bare Cells
PR1500LCDRT2U | CyberPower | RB1270X4F | 4 x 12V 7Ah F2 | 34.3 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/pr1500lcdrt2u/ | Order Bare Cells
PR1500LCD | CyberPower | RB12170X2A | 2 x 12V 17Ah NB | 76.2 | No verified LiFePO4 fit | NB | verified | No serial split found | https://cellfitups.com/ups/pr1500lcd/ | Order Bare Cells
OL1500RTXL2U | CyberPower | RB1290X3L | 3 x 12V 9Ah F2 | 45.7 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/ol1500rtxl2u/ | Order Bare Cells
SMT1000RM2UC | APC | APCRBC157 | 4 x 12V 7.2Ah F2 | 35.6 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/smt1000rm2uc/ | Order Bare Cells
SUA1500RM2U | APC | RBC24 | 4 x 12V 9Ah F2 | 49.8 | No verified LiFePO4 fit | F2 | verified | No serial split found | https://cellfitups.com/ups/sua1500rm2u/ | Order Bare Cells